## Sheet1
ESTIMATED RANGE OF SERVICE PRESSURES, IN THE POTABLE WATER SYSTEM
TABLE OF MINIMUM AND MAXIMUM PRESSURES (Estimated Range of Residential Service Pressures in EMWD's Potable Water System)
CLARIFICATIONS & DIRECTIONS TO FILL OUT THIS FORM
1- Intended Uses of this Form:
a- For residential tracts only (not for commercial, industrial, institutional, etc…)
b- Issuance of EMWD's Low/High Service Pressure Notices/Agreements for residential services
(where Low Pressure is <40 psi, High Pressure is >80 psi)
c- Identify available pressure (in the Main) to facilitate the design of private residential Fire Sprinkler Systems.
While the tabulated pressure values take into account the proposed pad elevations, other factors must also
be considered by the project's sponsor as noted below:
The project sponsor is responsible to calculate the available on-site service pressures, commencing from the point of connection(s) in EMWD’s main pipeline(s), including lateral(s), meter(s), and all post meter/appurtenances (e.g. DCDA’s, RPDA’s, PRV's), taking into consideration resulting minor and friction head losses (such as elbows, tees, valves, and pipe diameter/length/material), pad elevations, and building height, such that the pressure delivered to each floor level and customer is adequate to meet jurisdictional requirements.
d- Proper sizing of service laterals (1.5" lateral for pressures <50 psi; 1.0" for pressure=>50 psi)
e- Include this (signed and sealed) table in the Index Sheet of the approved plans
f- This table is NOT intended to provide Hydrant-Flow results within the tract. Fire Flow test results are shown
in separate documents, namely, the Hydraulic Boundary Conditions form and/or the Fire Flow test Report.
2- Prior to filling out this form, The project's Engineer of Record shall request EMWD's Hydraulic Boundary Conditions report at defined Point(s) Of Connection (POC)
3- The project's Engineer of Record shall fill out these tables, based on reference data from EMWD's Hydraulic Boundary Conditions report at the referenced Point(s) Of Connection (POC)
4 -How To Fill Out this Form:
a- While it is preferable to fill out the YELLOW cells (containing BLUE TEXT) to preserve the integrity of results in the remaining cells (which contain nested-equations), the Engineer of Record may modify these equations as he/she deems necessary.
b- While the nested equations under the "(lowest/Highest) HGL" columns are set to produce the lowest/highest HGL values from EMWD's Reference Data, the Engineer of Record may elect to edit these quations to produce an average HGL value, or insert other equations as he/she deems necessary.
c- Copy/paste nested equations as new rows are inserted for additional lots
d- Unless editing is necessary, do not over-write nested-equations in the following columns: "Min Pressure", "Max Pressure", "HGL", "Lowest HGL", "Min Lateral Size", "Highest HGL" & "Low, Normal or High Pressure"
e- Provide a companion map, identifying lot locations, lot numbers, pad elevations, and POCs
5- Prior to EMWD's final plan approval, the Engineer of Record shall verify that the referenced Hydraulic Boundary Conditions report is current, and shall update these tables accordingly if a new report is required.
TABLE OF MINIMUM AND MAXIMUM PRESSURES (Estimated Range of Residential Service Pressures in EMWD's Potable Water System)
Project Name:
EMWD's Design Conditions Work Order: | [5 empty] | EMWD's Project Reference Number:
EMWD's Reference Data(1):
|  | POC Location | Elevation (ft) | Min Pressure (psi) | HGL(1) (ft) | Max Pressure (psi) | HGL(1) (ft)
(1) EMWD's reference data shall be obtained from the Hydraulic Boundary Conditions report, which should be requested from EMWD prior to preparing this form
Location(s):
Pressure Zone HWL:
Date provided by EMWD:
Detailed Min & Max Service Pressures Table
| Lot Number | Street Elevation at the Main (ft) | Min Pressure (psi) | (lowest) HGL (ft) | Min Lateral Size | Max Pressure (psi) | (highest) HGL (ft) | Low, Normal, or High Pressure
|  |  | contains nested equations | contains nested equations | contains nested equations | contains nested equations | contains nested equations | contains nested equations
Prepared By:
Date Prepared:
Sign and Seal of Engineer Of Record
FORM: NBD-071
Rev. 1/3/2022
FORM: NBD-071
Rev. 3/11/2022
Sample
Sample