## Summary
Estimated Local Supplies Available (AF)(1),(3) |  |  |  | Estimated Demands - Average of 2013/2014 (AF)
Supply | 2017 | 2018 | 2019 | Demand Type | 2017 | 2018 | 2019
Groundwater(2) | 15269.1087 | 14709.7827 | 14556.5754 | Retail Demands | 88969 | 88969 | 88969
Desalination(2) | 7287.895 | 7287.895 | 7287.895 | Estimated Wholesale Demands(4) | 30440 | 32307 | 33389
Estimated Imported Supplies Available (AF) |  |  |  | Estimated Demands (Retail + Wholesale) | 119409 | 121276 | 122358
Supply | 2017 | 2018 | 2019 | Balance (negative = surplus) | -365.0037 | -526.6777 | -539.4704
Metropolitan Water District | 97217 | 99805 | 101053
Retail Supply / Demand Comparison
Total Potable Supplies | 119774.0037 | 121802.6777 | 122897.4704 | Supply / Demand | 2017 | 2018 | 2019
|  |  |  | Retail Demands | 88969 | 88969 | 88969
|  |  |  | Retail Potable Supply | 89334.0037 | 89495.6777 | 89508.4704
|  |  |  | Balance (negative = surplus) | -365.0037 | -526.6777 | -539.4704
[6 empty] | Conservation Standard (supply shortfall as a percentage of demand in 2019) | 0%
Notes
(1) EMWD expects similar supplies to be available on a "water year" and "calendar year" basis since the source of the local supplies comes from water in storage. Essentially, supplies available in each 12 month period will be the same.
(2) Assumptions made for each of the local supplies are documented on their respective tabs
(3) These supplies are for the potable system only
(4) Wholesale demands to be met from MWD water. Quantity determined via coordination with wholesale agencies (details posted at: http://www.emwd.org/home/showdocument?id=14751 per SWRCB requirements)
General Comments
Eastern Municipal Water District (EMWD) is certifying that it is able to supply enough potable water to meet 100 percent of estimated customer demand over the next three years. This is possible through long-term planning and implementation of robust measures for both water supply and demand management. EMWD and its customers have invested in a diverse portfolio of local resources, regional supplies and storage, and active and varied conservation program that reduced its gallon per capita per day water use by 25 percent prior to 2013. Part of EMWD’s investments in local resources is our extensive recycled water system. Recycled water currently meets 29 percent of EMWD’s total demand. EMWD utilizes 100 percent of its recycled water within its service area. Over 35,000 acre feet of recycled water was used to meet the demands of agricultural, landscape, environmental, and industrial customers in 2015. This has reduced the demand for imported potable water and increased reliability for EMWD’s customers. The reduction in demand is reflected in the 2013 and 2014 average demand used to test reliability. In addition to the projects completed prior to 2013, EMWD has invested in an accelerated recycled water program since 2013 that when completed will permanently offset 950 acre-feet of potable water demand. The certification of our ability to meet customer demand does not reduce EMWD’s focus on conservation during the current drought. The Governor’s Executive Order and Emergency Regulation remain in effect and EMWD will continue to implement conservation programs and message to customers the need to save water. We estimate our efforts will reduce water demand between 10 and 20 percent this summer over 2013. These efforts include: • Remaining at Stage 3c of our Water Shortage Contingency Plan. This eliminates our “Excessive” tier and requires customer to pay our highest water rate ($11.16/CCF) for use over their water budget; • Utilizing EMWD and grant funding to continue rebating the conversion of non-functional turf in highly visible areas to save water and influence public opinion; • Offering assistance to all customer groups to reduce outdoor watering including installing high efficiency irrigation nozzles and smart controllers; • Continuing to enforce water waste restrictions through warnings and penalties; • Accelerating the conversion of potable water landscape customer to the recycled water system; and • Sending strong messaging to customers about the on-going need for conservation. The reduction of our Conservation Standard does not impact EMWD’s strong commitment to ongoing conservation and water use efficiency. EMWD will continue work with its partners and stakeholder to make conservation way of life in our service area.

## Demands
Annual Potable Demands (AF)
Year | Demand
2013 | 88855
2014 | 89083
Average | 88969

## Well_Proj
Estimated Available Well Capacity by Individual Well (AF) | [8 empty] | Estimated Total Available Well Capacity by GMZ (AF)
Well Information |  | 2017 Pumping |  | 2018 Pumping |  | 2019 Pumping |  |  | GMZ |  | 2017 | 2018 | 2019
Well | GMZ | % Capacity(1) | GW Avail. | % Capacity(1) | GW Avail. | % Capacity(1) | GW Avail. |  | Name | Wells | Total | Total | Total
EMWD 14 Riverbed | Upper Pressure | (out of service) | [5 empty] | HSJ | Canyon | 3 | 7006.9273 | 7004.1156 | 7001.3039
EMWD 17 Cienega | Canyon | 85.62% | 1924.6052 | 85.49% | 1921.7935 | 85.37% | 1918.9818 | HSJ | Hemet South | 1 | 1322.7069 | 1322.7069 | 1322.7069
EMWD 25 Fruitvale | Upper Pressure | 100% | 1876.5497 | 100% | 1876.5497 | 100% | 1876.5497 | WSJ | Perris North | 4 | 5225.8795 | 5239.5245 | 5253.1694
EMWD 26 Cienega | Canyon | 100% | 3192.7408 | 100% | 3192.7408 | 100% | 3192.7408 | HSJ | Upper Pressure | 10 | 13636.9268 | 13843.312 | 13981.491
EMWD 27 Hewitt/Evans | Upper Pressure | (out of service)
EMWD 29 New Quandt | Upper Pressure | 100% | 2032.9288 | 100% | 2032.9288 | 100% | 2032.9288 |  | Estimated Total Available Well Capacity by Management Plan Area (AF)
EMWD 33 Mountain | Upper Pressure | 90.05% | 1179.3314 | 91.24% | 1194.9228 | 92.43% | 1210.5142 |  | Name | Wells | 2017 | 2018 | 2019
EMWD 34 Cienega | Canyon | 100% | 1889.5813 | 100% | 1889.5813 | 100% | 1889.5813 |  | HSJ | 14 | 21966.561 | 22170.1344 | 22305.5018
EMWD 35 Palm/Menlo | Hemet South | 100% | 1322.7069 | 100% | 1322.7069 | 100% | 1322.7069 |  | WSJ | 4 | 5225.8795 | 5239.5245 | 5253.1694
EMWD 36 Washington | Upper Pressure | 95.28% | 1589.3467 | 97.91% | 1633.1863 | 100% | 1668.0442
EMWD 55 Perris II | Perris North | 87.44% | 951.5164 | 88.7% | 965.1613 | 89.95% | 978.8062 |  |  | HSJ ABPR + Bank Usage(3) | 10043.2291 | 9470.2583 | 9303.4061
EMWD 56 New Perry | Perris North | 100% | 1511.665 | 100% | 1511.665 | 100% | 1511.665
EMWD 57 New Follico | Perris North | 100% | 1309.6753 | 100% | 1309.6753 | 100% | 1309.6753 |  | Estimated Total Available Well PRODUCTION (AF)
EMWD 59 Indian | Perris North | 100% | 1453.0228 | 100% | 1453.0228 | 100% | 1453.0228 |  | Management Plan Area |  | 2017 | 2018 | 2019
EMWD 80 Seventh | Upper Pressure | 92.95% | 775.188 | 93.51% | 779.8753 | 94.07% | 784.5626 |  | Hemet/San Jacinto (HSJ)(4) |  | 10043.2291 | 9470.2583 | 9303.4061
EMWD 90 Evans/Old Mountain | Upper Pressure | 97.73% | 2553.6105 | 100% | 2612.8348 | 100% | 2612.8348 |  | West San Jacinto (WSJ) |  | 5225.8795 | 5239.5245 | 5253.1694
EMWD 91 Ramona/Esplanade | Upper Pressure | 86.32% | 2131.7486 | 89.12% | 2200.7489 | 91.91% | 2269.7493
EMWD 92 Ramona/Hemet | Upper Pressure | 93.85% | 1498.2232 | 94.73% | 1512.2653 | 95.61% | 1526.3075 |  |  | Total | 15269.1087 | 14709.7827 | 14556.5754
|  |  | 27192.4406 |  | 27409.6589 |  | 27558.6712
Notes
(1) A well's ability to pump water is dependent on multiple factors, including but not limited to, the depth and pump curve of the installed pump, intra-well gradients (caused by differential hydraulic head - wells are screened across multiple aquifers), time since well was last rehabilitated and the influence zone of nearby wells. For the purpose of this analysis, a given well's current capacity (June 2016) was assumed to be its full capacity. The given well's available production was reduced proportionally based on the amount of screen that is estimated to be within saturated aquifer.
(2) The amount of saturated aquifer at a given well location was estimated assuming a repeat of the trends from 2013 - 2016, with starting conditions being current day 2016. Water level data used at each well were picked to be as close to June as possible given SWRCB guidelines. If, for a given well and year, only a pumping water level was available, then a pumping water level was selected for the other year to ensure consistency. Generally speaking, static water levels are considered to be more representative of aquifer conditions. However, all water levels used in this analysis may be affected by the influence of nearby wells. Use of pumping water levels (if static water levels are not available) skew the results conservatively as the results of calculations using pumping water levels will show less volume in storage due the the impact of the pumping well's local cone of depression.
(3) Well pumping in Hemet/San Jacinto wells is limited by adjusted base production rights (ABPR) set by the Hemet-San Jacinto Watermaster. EMWD has received credit for historic recharge in the HSJ area and can exceed its annual ABPR by withdrawing from "banked" water. EMWD plans to use at least 2,000 AF annually from "banked" water from the HSJ Management Plan Area. EMWD pumping in the West San Jacinto Management Plan Area is limited only by well capacity
(4) HSJ Pumping was assumed to be the lesser of estimated well capacity available or the sum of the HSJ ABPR and planned bank usage. In every year, the limitation was the ABPR rather than capacity of the wells

## Well_Levels
[10 empty] | "Critical" Screen Condition | 50%
Groundwater production in the Hemet/San Jacinto portion of the San Jacinto Groundwater Basin is not limited by well capacity, but by adjusted base production rights set by the Hemet-San Jacinto Watermaster.
Groundwater Levels (feet below reference point) | [14 empty] | Projected Groundwater Levels(4)
Well Information |  | 2013 Levels |  |  | 2016 Levels |  |  |  |  | "Critical" Depths(1) |  | Other Levels of Note |  |  | Avg ∆(2) | 2017 Levels(3) |  | 2018 Levels |  | 2019 Levels
Well Name | GMZ | Date | Depth to Water | Type | Date | Depth to Water | Type | ∆ 2013 | Avg. Yr ∆ | Depth | ∆ 2016 | Date | Depth to Water | Type | ∆ (ft) | Est. Depth | % Screen | Est. Depth | % Screen | Est. Depth | % Screen
EMWD 14 Riverbed | Upper Pressure |  |  |  | (out of service) | [6 empty] | 2016-04-25 | 514.1 | Static | #N/A | (out of service)
EMWD 17 Cienega | Canyon |  |  |  | 2016-04-12 | 208 | Static | #N/A |  | 589 | 381 | 2014-09-17 | 248.2 | Static | -1.3333 | 209.3333 | 85.62% | 210.6667 | 85.49% | 212 | 85.37%
EMWD 25 Fruitvale | Upper Pressure | 2013-05-21 | 455 | Static | (could not sound) | [9 empty] | 13.6524 | 400.3905 | 100% | 386.7381 | 100% | 373.0857 | 100%
EMWD 26 Cienega | Canyon | 2013-01-25 | 134.2 | Static | 2016-04-12 | 206.8 | Static | 72.6 | 24.2 | 905 | 698.2 | 2013-06-27 | 294.4 | Pumping | 24.2 | 182.6 | 100% | 158.4 | 100% | 134.2 | 100%
EMWD 27 Hewitt/Evans | Upper Pressure |  |  |  | 2016-04-11 | 369 | Static | #N/A |  | 1020 | 651 | 2014-09-17 | 367.2 | Static | 13.6524 | (out of service)
EMWD 29 New Quandt | Upper Pressure |  |  |  | 2016-04-19 | 390.4 | Static | #N/A |  | 1000 | 609.6 | 2013-06-30 | 423 | Pumping | 13.6524 | 376.7476 | 100% | 363.0952 | 100% | 349.4429 | 100%
EMWD 33 Mountain | Upper Pressure | 2013-06-26 | 453 | Static | 2016-02-03 | 478 | Static | 25 | 8.3333 | 750 | 272 |  |  |  | 8.3333 | 469.6667 | 90.05% | 461.3333 | 91.24% | 453 | 92.43%
EMWD 34 Cienega | Canyon | 2013-02-26 | 144 | Static | 2016-04-12 | 208 | Static | 64 | 21.3333 | 490 | 282 | 2013-06-26 | 281.4 | Pumping | 21.3333 | 186.6667 | 100% | 165.3333 | 100% | 144 | 100%
EMWD 35 Palm/Menlo | Hemet South | 2013-06-26 | 253 | Static | 2016-04-20 | 249 | Static | -4 | -1.3333 | 390 | 141 |  |  |  | -1.3333 | 250.3333 | 100% | 251.6667 | 100% | 253 | 100%
EMWD 36 Washington | Upper Pressure | 2013-03-27 | 477.2 | Static | 2016-04-15 | 518.2 | Static | 41 | 13.6667 | 740 | 221.8 | 2013-06-27 | 514.2 | Pumping | 13.6667 | 504.5333 | 95.28% | 490.8667 | 97.91% | 477.2 | 100%
EMWD 55 Perris II | Perris North | 2013-06-20 | 161.1 | Pumping | 2016-04-05 | 169 | Pumping | 7.9 | 2.6333 | 245 | 76 |  |  |  | 2.6333 | 166.3667 | 87.44% | 163.7333 | 88.7% | 161.1 | 89.95%
EMWD 56 New Perry | Perris North | 2013-06-20 | 103.8 | Pumping | 2016-04-05 | 102 | Pumping | -1.8 | -0.6 | 490 | 388 |  |  |  | -0.6 | 102.6 | 100% | 103.2 | 100% | 103.8 | 100%
EMWD 57 New Follico | Perris North | 2013-06-19 | 96.1 | Pumping | (could not sound) | [6 empty] | 2015-01-14 | 65 | Static | 0.88889 | 92.5444 | 100% | 91.6556 | 100% | 90.7667 | 100%
EMWD 59 Indian | Perris North | 2013-06-20 | 96.7 | Pumping | 2016-04-12 | 92 | Pumping | -4.7 | -1.5667 | 462.5 | 370.5 |  |  |  | -1.5667 | 93.5667 | 100% | 95.1333 | 100% | 96.7 | 100%
EMWD 80 Seventh | Upper Pressure | 2013-06-13 | 441 | Static | 2016-04-15 | 455.5 | Static | 14.5 | 4.8333 | 820 | 364.5 |  |  |  | 4.8333 | 450.6667 | 92.95% | 445.8333 | 93.51% | 441 | 94.07%
EMWD 90 Evans/Old Mountain | Upper Pressure | 2013-06-26 | 495 | Pumping | 2016-04-15 | 536.2 | Pumping | 41.2 | 13.7333 | 785 | 248.8 |  |  |  | 13.7333 | 522.4667 | 97.73% | 508.7333 | 100% | 495 | 100%
EMWD 91 Ramona/Esplanade | Upper Pressure | 2013-07-31 | 515 | Pumping | 2016-04-19 | 572 | Pumping | 57 | 19 | 800 | 228 |  |  |  | 19 | 553 | 86.32% | 534 | 89.12% | 515 | 91.91%
EMWD 92 Ramona/Hemet | Upper Pressure | 2013-02-27 | 511.6 | Static | 2016-04-20 | 530.6 | Static | 19 | 6.3333 | 840 | 309.4 |  |  |  | 6.3333 | 524.2667 | 93.85% | 517.9333 | 94.73% | 511.6 | 95.61%
Notes
(1) The groundwater portion of Worksheet 1 asks for the amount of water that can be withdrawn "without substantially affect your ability to pump water". For the purposes of this analysis, a condition creating a "substantial" effect on "ability to pump water" was defined as existing when over 50 percent of a well's screened interval was exposed. In reality, the ability to pump water is dependent on multiple factors, including but not limited to, the depth and pump curve of the installed pump, intra-well gradients (caused by differential hydraulic head - wells are screened across multiple aquifers), time since well was last rehabilitated and the influence zone of nearby wells.
(2) The average annual change in water level was calculated using the difference between referenced water levels in 2013 and 2016. If a water level was not available for a specific well, an average of the change for all the wells with records within the same groundwater management zone were used.
(3) For wells without recorded levels in either 2013 or 2016, data was estimated. For example, 2017 water level data for wells with level data available in 2013 but not in 2016 was estimated by adding four years worth of average annual water level change as calculated by the average of other wells within the same groundwater management zone.
(4) Projected groundwater levels should be compared only against the same well or against wells with the same pumping condition within the same groundwater management zone, since a mixture of static and pumping groundwater levels were used to "best fit" the analysis timeline set by the SWRCB. Generally, static water levels are considered more representative of an aquifer's status than a pumping water level, however, where pumping water levels were the only dataset available in either 2013 or 2016, a matching level was found to generate as close to a direct comparison as possible. This analysis does not capture the potential influence of pumping from nearby wells when the water levels were measured.

## Well_Prod
| Downtime | 10% | 1 cfs | 1.9835 | AFd
EMWD Well Pumping Capacity(3) |  |  | HSJ Production Rights(4)
Well | cfs(1) | AFY(2) | Year | ABPR | Bank Usage(5) | Total HSJ GW
EMWD 14 Riverbed | 0 | 0 | 2017 | 8043.2291 | 2000 | 10043.2291
EMWD 17 Cienega | 3.45 | 2247.9501 | 2018 | 7470.2583 | 2000 | 9470.2583
EMWD 25 Fruitvale | 2.88 | 1876.5497 | 2019 | 7303.4061 | 2000 | 9303.4061
EMWD 26 Cienega | 4.9 | 3192.7408
EMWD 27 Hewitt/Evans | 0 | 0
EMWD 29 New Quandt | 3.12 | 2032.9288
EMWD 33 Mountain | 2.01 | 1309.6753
EMWD 34 Cienega | 2.9 | 1889.5813
EMWD 35 Palm/Menlo | 2.03 | 1322.7069
EMWD 36 Washington | 2.56 | 1668.0442
EMWD 55 Perris II | 1.67 | 1088.1382
EMWD 56 New Perry | 2.32 | 1511.665
EMWD 57 New Follico | 2.01 | 1309.6753
EMWD 59 Indian | 2.23 | 1453.0228
EMWD 80 Seventh | 1.28 | 834.0221
EMWD 90 Evans/Old Mountain | 4.01 | 2612.8348
EMWD 91 Ramona/Esplanade | 3.79 | 2469.4873
EMWD 92 Ramona/Hemet | 2.45 | 1596.3704
| Annual Total | 28415.3929
Notes
(1) Pumping capacity in cfs is maximum instantaneous flow based on current condition of well
(2) Pumping capacity in AFY is the hypothetical annual capacity of the well assuming a 365 day year and well downtime of 10%
(3) Well pumping in Hemet/San Jacinto wells is limited by adjusted base production rights (ABPR) set by the Hemet-San Jacinto Watermaster. For each year of this analysis, the supplies available out of the HSJ wells will be the lesser of the estimated capacity and the ABPR.
(4) EMWD has received credit for historic recharge in the HSJ area and can exceed its annual ABPR by withdrawing from "banked" water
(5) EMWD plans to use at least 2,000 AF annually from "banked" water from the HSJ Management Plan Area
(6) EMWD pumping in the West San Jacinto Management Plan Area is limited only by well capacity

## Well_Info
Well Information / Construction
Well | GMZ | RP Elev | Top Perf | Bot Perf | Screen
EMWD 14 Riverbed | Upper Pressure | 1618 | 252 | 1000 | 748
EMWD 17 Cienega | Canyon | 1666.4 | 56 | 1122 | 1066
EMWD 25 Fruitvale | Upper Pressure | 1592 | 470 | 1530 | 1060
EMWD 26 Cienega | Canyon | 1667.2 | 350 | 1460 | 1110
EMWD 27 Hewitt/Evans | Upper Pressure | 1575 | 364 | 1676 | 1312
EMWD 29 New Quandt | Upper Pressure | 1524 | 470 | 1530 | 1060
EMWD 33 Mountain | Upper Pressure | 1603 | 400 | 1100 | 700
EMWD 34 Cienega | Canyon | 1670.8 | 370 | 610 | 240
EMWD 35 Palm/Menlo | Hemet South | 1565 | 300 | 480 | 180
EMWD 36 Washington | Upper Pressure | 1654 | 480 | 1000 | 520
EMWD 55 Perris II | Perris North | 1450 | 140 | 350 | 210
EMWD 56 New Perry | Perris North | 1461 | 240 | 740 | 500
EMWD 57 New Follico | Perris North | 1445 | 220 | 600 | 380
EMWD 59 Indian | Perris North | 1456 | 260 | 665 | 405
EMWD 80 Seventh | Upper Pressure | 1583 | 390 | 1250 | 860
EMWD 90 Evans/Old Mountain | Upper Pressure | 1613 | 510 | 1060 | 550
EMWD 91 Ramona/Esplanade | Upper Pressure | 1631 | 460 | 1140 | 680
EMWD 92 Ramona/Hemet | Upper Pressure | 1641 | 480 | 1200 | 720

## Desalination_Well_Prod
EMWD Brackish Well Production (AF) |  | EMWD Desalter Production (AF)
Well | 2015 | Desalter | 2015
EMWD 75 Salt Creek | 463.477 | Perris & Menifee Desalters | 7287.895
EMWD 76 McLaughlin | 2095.899
EMWD 81 Antelope/Watson | 1193.134
EMWD 82 Mapes/Sherman | 1159.558
EMWD 83 Ellis/Sherman | 1170.356
EMWD 84 Ellis/Bradley | 736.424 | Projected Desalter Production (AF)
EMWD 85 Murrieta/Salt Creek | 392.758 | Desalter | 2017 - 2019
EMWD 86 Murrieta/San Jacinto | 1661.539 | Perris & Menifee Desalters | 7287.895
EMWD 87 Nuevo/Olivas | 800.403
EMWD 88 Pico/San Jacinto | 412.767
EMWD 89 Ethanac II | 2.649
Annual Totals | 10088.964
Notes
(1) Brackish water is pumped from portions of the West San Jacinto Management Plan area
(2) Water levels in the WSJ area have been rising or stable for an extended period of over 10 years (see "Brackish_GW_Levels" tab)
(3) Supply available from desalters assumed to be constant (equal to 2015) for the purpose of this analysis (since brackish groundwater levels are stable or trending upward)
(4) More information on EMWD's desalination program can be found in EMWD's submittal for a conservation standard adjustment in March 2016 located here: http://www.drinc.ca.gov/DNN/Portals/0/ORPP/EMWD_NewLocalSupply_Description_20160218_3-1-2016%208-11-48%20AM.pdf

## Brackish_GW_Levels
Average Groundwater Level (Depth to Water)
Year | Total WSJ GW Production (AF) | Lakeview GMZ | Menifee GMZ | Perris North GMZ | Perris South GMZ | San Jacinto Lower Pressure GMZ
1995 | 18810.3 | 259.17 | 97.6653 | 129.2317 | 49.2724 | 162.5969
1996 | 22084.03 | 256.0198 | 99.6286 | 137.1244 | 54.5914 | 187.0512
1997 | 25007.26 | 248.8437 | 103.2446 | 123.9772 | 60.8244 | 191.7794
1998 | 18660.56 | 248.9675 | 96.927 | 108.7018 | 54.8638 | 191.133
1999 | 22652.55 | 242.3245 | 95.4152 | 118.0982 | 57.6436 | 182.2833
2000 | 23102.76 | 235.2508 | 102.1829 | 114.5554 | 54.5916 | 182.4424
2001 | 19830.9821 | 232.4148 | 101.1222 | 103.7343 | 52.4861 | 185.7323
2002 | 20606.067 | 226.087 | 106.4591 | 104.01 | 53.456 | 171.88
2003 | 18579.5591 | 220.515 | 106.0977 | 112.159 | 48.4496 | 159.8419
2004 | 18648.605 | 211.7949 | 108.5045 | 81.7479 | 47.8357 | 165.4795
2005 | 15297.609 | 204.2721 | 102.3095 | 98.1557 | 42.4561 | 159.5882
2006 | 23053.89 | 202.9846 | 101.865 | 92.3506 | 43.9484 | 160.5605
2007 | 22625.9033 | 189.5561 | 106.1162 | 60.9612 | 50.3168 | 156.3674
2008 | 19084.0379 | 180.1357 | 105.7972 | 92.3762 | 53.2274 | 160.5068
2009 | 16924.123 | 178.4281 | 102.925 | 73.7265 | 53.836 | 158.4457
2010 | 18867.86 | 183.8448 | 94.8583 | 92.016 | 50.7325 | 157.6467
2011 | 20127.1806 | 182.3123 | 90.075 | 80.9349 | 50.9904 | 156.1881
2012 | 20754.879 | 179.4774 | 88.0706 | 81.2279 | 50.6728 | 152.0244
2013 | 21767.35 | 172.9188 | 91.903 | 66.6264 | 53.6799 | 127.0606
2014 | 24112.511 | 183.863 | 96.3871 | 70.8432 | 51.2427 | 142.5143
2015 | 20004.033 | 174.9483 | 92.6909 | 73.1283 | 49.0361 | 137.3475
Historic Well Production (AF/year)
Year | Lakeview GW Prod | Menifee GW Prod | Perris North GW Prod | Perris South GW Prod | San Jacinto Lower Pressure GW Prod
1995 | 8372.1 | 4241.51 | 3614.56 | 1658.44 | 923.69
1996 | 8968.72 | 4360.43 | 6396.5 | 1374.59 | 983.79
1997 | 9214.65 | 4240.69 | 9120.55 | 1502.61 | 928.76
1998 | 6214.61 | 3883.7 | 6607.68 | 1137.83 | 816.74
1999 | 7451.63 | 4730.64 | 8679.67 | 1195.89 | 594.72
2000 | 6393.47 | 4829.53 | 9494.25 | 1505.8 | 879.71
2001 | 4776.881 | 5019.7331 | 8488.599 | 610.17 | 935.599
2002 | 5313.461 | 5477.19 | 8053.073 | 1077.693 | 684.65
2003 | 3395.397 | 5115.73 | 7748.28 | 1869.75 | 450.4021
2004 | 3941.9811 | 4538.38 | 7507.723 | 2315.7804 | 344.7405
2005 | 2915.128 | 4405.83 | 5821.631 | 1842.98 | 312.04
2006 | 3048.639 | 4859.44 | 8283.561 | 6454.66 | 407.59
2007 | 2790.4691 | 4724.2802 | 8065.474 | 6629.54 | 416.14
2008 | 2213.8559 | 4131.1953 | 8424.12 | 4166.04 | 148.8266
2009 | 2118.89 | 1420.99 | 6788.585 | 6367.46 | 228.198
2010 | 2596.85 | 3827.99 | 5531 | 6712.08 | 199.94
2011 | 2763.07 | 4306.69 | 6111.92 | 6770.43 | 175.0706
2012 | 2901.339 | 4189.33 | 7029.32 | 6390.52 | 244.37
2013 | 3831.262 | 4228.673 | 6358.989 | 6280.911 | 1067.515
2014 | 4968.409 | 3684.859 | 5183.098 | 9108.057 | 1168.088
2015 | 3832.1 | 709.596 | 5669.813 | 9288.561 | 503.963